This is to certify that Essential Pump and Well service performed a well test at the property address stated as: 4286 Hwy 41 East, Atascadero CA.

The test was performed by Rocky Greene on the date of 5-8-26

| Datum point: | Well Head, 6” casing |
| --- | --- |
| Static level: | 70’ |
| Pump setting: | 160’ |
| Well depth: | 175 |
| Horsepower: | 2 hp |
| Flow method: | Bucket test |
| Length of test: | 4 hour |

The test results are as follows:

| Time: | Flow Rate (gpm): | Water Level (ft): | Notes: |
| --- | --- | --- | --- |
| 11:00 | 42.8 | 70 | Clear, no odor and clean |
| 11:05 | 42.8 | 74 |  |
| 11:10 | 42.8 | 76 |  |
| 11:15 | 42.8 | 77 |  |
| 11:20 | 42.8 | 80 |  |
| 11:25 | 42.7 | 85 |  |
| 11:30 | 42.7 | 85 |  |
| 11:45 | 42.7 | 85 |  |
| 12:00pm | 42.7 | 85 |  |
| 12:15 | 42.7 | 85 |  |
| 12:30 | 42.7 | 85 |  |
| 12:45 | 42.6 | 85 |  |
| 1:00 | 42.6 | 85 |  |
| 1:30 | 42.6 | 85 |  |
| 2:00 | 42.6 | 85 |  |
| 2:30 | 42.6 | 85 |  |
| 3:00 | 42.6 | 85 | End test |
| 3:05 | 0 | 77 | Start recovery test |
| 3:10 | 0 | 70 |  |
| 3:15 | 0 | 70 | End recovery test |